## Slide 1
Energy Autonomy of Building
as the Basis for More Efficient
Electromobility
J. Šimčák
Department of Electric Power Engineering, Faculty of Electrical Engineering and Informatics, Technical University of Košice
Nanogrids · Microgrids · V2G/V2B · Photovoltaics · BESS

## Slide 2
AGENDA
What we'll cover today
01
Motivation
Decentralized energy systems and the role of electromobility
02
Nanogrid & microgrid
Architecture, control, island mode operation
03
Electromobility in the grid
V2G / V2B as a mobile energy storage asset
04
Building model design
PV, BESS, EV infrastructure, control system
05
Results
Consumption and generation balance, impact of EV charging
06
Conclusions
Benefits and challenges
02

## Slide 3
01 · INTRODUCTION & MOTIVATION
Electromobility as part of the building energy system
The shift toward decentralized energy systems is driving the growth of nanogrids — small, autonomous systems that manage local generation, storage and consumption within buildings. Electric vehicles with bidirectional charging (V2G/V2B) are becoming mobile energy storage units, increasing both flexibility and resilience of the building.
☀
PV + ESS
Local generation and storage of energy directly in the building
🔋
V2G / V2B
Electric vehicle as a mobile, bidirectional storage asset
🌐
P2P exchange
Energy sharing between interconnected nanogrids
40%
of global energy consumption is attributed to buildings
EU Energy Performance of Buildings Directive (EPBD): new buildings must be nZEB (nearly zero-energy), min. 25% from RES.
03

## Slide 4
02 · NANOGRID & MICROGRID
What is a nanogrid?
A nanogrid is the fundamental building block of decentralized energy systems — a small local system serving a single building, household or small enterprise. It includes its own generation (e.g. PV), storage (batteries) and control electronics. The goal is to cover local consumption, increase self-sufficiency and enable intelligent management of generation and demand.
Nanogrid schematic
Renewable
sources
Non-renewable
sources
Energy
storage
Nanogrid controller
Gateway
External power entity / grid
Loads: Load 1, Load 2, …, Load n
04

## Slide 5
02 · NANOGRID & MICROGRID
DC vs. AC nanogrids
DC nanogrid
Electricity flows directly, as direct current, from PV and batteries to the load
Fewer conversions → higher overall efficiency (often > 90%)
Best suited when both sources and loads operate on DC voltage
Drawback: limited availability of DC-compatible appliances, requires a bidirectional AC–DC converter
AC nanogrid
Compatible with most standard household and commercial appliances
Easier integration into existing building wiring
Multiple energy conversions (DC→AC) reduce efficiency
Broad availability of AC appliances and existing grid infrastructure
A critical feature of both types: the ability to operate in island mode during outages — control ranging from local algorithms (droop control) to communication-enabled decentralized optimization.
05

## Slide 6
02 · NANOGRID & MICROGRID
From nanogrid to microgrid
A microgrid is a larger, localized energy system capable of autonomous operation or coordination with the main grid — typically serving neighbourhoods, campuses, industrial parks or military bases. Nanogrids act as its modular elements, interconnected via a common backbone (AC/DC), enabling aggregation of generation and consumption, dynamic load balancing and peer-to-peer energy exchange.
PV, wind turbines, Combined Heat and Power (CHP), storage systems and power electronic converters
Layered control system: voltage and frequency stability, seamless transition between grid-connected and islanded modes
Real-time monitoring and communication infrastructure for efficient system responsiveness
Nanogrid 1
Nanogrid 2
Nanogrid 3
Nanogrid 4
Microgrid
Main grid
06

## Slide 7
03 · ELECTROMOBILITY IN THE GRID
Electric vehicles as mobile storage
Electric vehicles within a microgrid provide mobile, distributed storage. With bidirectional charging (V2G, V2B), they can absorb surplus generation and supply energy back to the building or grid. Integrated into microgrid control systems, EVs enhance load balancing, provide ancillary services, and support critical systems during outages.
⚡
V2B — Vehicle-to-Building
EV supplies energy directly to the building during peak demand or an outage
⚡
V2G — Vehicle-to-Grid
EV supplies energy back to the distribution grid, supporting its stability
Benefits for the building
Load balancing · support for critical systems during a grid outage
07

## Slide 8
03 · ELECTROMOBILITY IN THE GRID
Context: distributed generation (DG)
Conventional systems rely on large-scale, fossil-fuel-based generation delivered over long distances. This model is inadequate for a low-carbon transition — and over 1 billion people worldwide still lack access to electricity, mainly due to the economic impracticality of extending the grid to remote areas. Distributed generation from renewable sources, located closer to the point of consumption, reduces transmission losses and improves delivery reliability.
“A nanogrid as the next evolutionary step — a compact, single-building system that can use demand-side management (DSM) to dynamically adapt consumption to energy availability and load flexibility.”
1 bn+
people worldwide without access to electricity
Feldheim (Germany)
100% energy self-sufficiency through a locally managed microgrid
Urja Upatyaka (Nepal)
1,200 households with more reliable, cheaper power than the national grid (outages up to 16 h/day)
08

## Slide 9
04 · BUILDING MODEL DESIGN
Conceptual model of the smart building
A multi-purpose building (offices, laboratories, classrooms) with integrated nanogrid infrastructure and electromobility. Hybrid operation: grid-connected, yet capable of autonomous operation given sufficient RES and storage.
🏢
4 floors
≈10 office units per floor
🧪
Laboratories
High consumption – equipment, ventilation, processes
📚
Classrooms
Variable load – lighting, multimedia, computers
📊
Monitoring
Local units on every floor for real-time data
Each room's consumption is determined by its purpose: offices (low–medium), laboratories (high), classrooms (variable).
09

## Slide 10
04 · BUILDING MODEL DESIGN
Underground parking and EV infrastructure
A dedicated underground parking garage with 30 parking spaces, each equipped with a charging point. The infrastructure supports bidirectional charging (V2B/V2G), smart charging management aligned with PV generation, and automatic detection of connected vehicles.
EV / PHEV
Connected, bidirectional interaction with the nanogrid — active energy asset
ICE vehicle
Not connected — occupies space only, reduces available V2B capacity
30
parking spaces with a charging point
7 kW
AC charger / point
70 kW
max. aggregate V2B power
Smart charging aligns charging profiles with PV generation and the building's load.
10

## Slide 11
04 · BUILDING MODEL DESIGN
Photovoltaics and battery storage (BESS)
The design accounts for the local climate conditions of Košice (48.7°N), where the annual Global Horizontal Irradiation (GHI) averages 1,180 kWh/m².
200 kWp
Target installed PV capacity
1,000 m²
Required net active area (of 1,200 m² gross rooftop)
20%
Efficiency of monocrystalline modules (200 Wp/m²)
400 kWh
Capacity of the central BESS in the technical room
System integration
Smart inverters interfacing the PV array with both AC and DC buses
MPPT controllers and software for real-time optimization
BESS stores surplus during the day, discharges at peak demand or outage — supports peak shaving
11

## Slide 12
04 · BUILDING MODEL DESIGN
Electrical distribution and control system (BEMS)
DC distribution
PV integration, battery systems, DC loads (LED lighting, EV chargers) and energy-efficient internal electronics.
AC distribution
Conventional office equipment, HVAC systems and grid interfacing.
Building Energy Management System (BEMS)
Load prioritization based on room type, occupancy and time of day
EV charging scheduling aligned with PV generation
Energy source selection: PV, battery, EV storage or grid
Mode switching between grid-connected and islanded, based on prediction
Remote diagnostics and readiness for future integration with external energy markets or P2P trading.
12

## Slide 13
04 · BUILDING MODEL DESIGN
Nanogrid operational scenarios
01
Autonomous mode
High PV generation and/or sufficient support from EVs and BESS — the building operates independently from the grid
02
Grid-tied mode
Low generation or high demand — the building draws from the grid, or injects surplus if contractual terms allow
03
Emergency mode
Grid outage — critical loads (laboratories, control systems) supported by battery and EV reserves
04
Fallback mode
BESS depleted and no PV — switches to the grid; on a simultaneous blackout, the EMS initiates load shedding of non-critical circuits
13

## Slide 14
05 · RESULTS
Power balance and annual consumption
The power estimate follows a bottom-up approach per EN 15232. Theoretical peak demand: 221 kW without EVs, 431 kW at full use of all 30 chargers (worst case).
Chart: Projected annual energy use by load type (Table 2)
| Offices | Laboratories | Classrooms | HVAC | Common areas
Annual consumption (MWh) | 72 | 80 | 12 | 27 | 5
156 kW
realistic coincident peak without EVs
219 kW
realistic coincident peak with EVs (0.3 coincidence factor)
196 MWh
total projected annual building consumption
14

## Slide 15
05 · RESULTS
Generation assets, storage and EV charging scenarios
Table 3 — Installed capacity
Photovoltaics
Rooftop
200 kWp
BESS battery
Technical room
400 kWh
EV infrastructure
Underground garage
30 × AC 7 kW
PV capacity of 200 kWp estimated from a gross rooftop area of ≈1,200 m² (≈1,000 m² effective area). BESS 400 kWh sized to support critical loads for 2–4 hours.
Chart: Table 4 — Estimated annual EV charging consumption
| Light | Medium | High
Annual energy (MWh/year) | 11.5 | 34.5 | 69
15

## Slide 16
05 · RESULTS
Impact of electromobility on energy autonomy
Without EV charging
The building operates as a Net Positive Energy entity.
196 MWh
projected annual consumption
≈220 MWh
PV generation potential
≈24 MWh
annual energy surplus
The stationary BESS (400 kWh) is sufficient to bridge diurnal gaps, ensuring a high degree of self-sufficiency.
With EV charging (30 points)
A dual impact: increased load vs. a flexibility asset.
11.5–69 MWh
additional annual load from EV charging
Net-positive →
net-consuming
possible balance shift under high usage
+700–900 kWh
additional V2B capacity at 50% occupancy
V2B extends islanded operation capability and reduces PV curtailment — improving the self-consumption ratio despite the lower net annual balance.
16

## Slide 17
Thank you for your attention
J. Šimčák · julius.simcak@tuke.sk
Department of Electric Power Engineering, FEI TUKE